## Slide 1
Unit 8
Basic Relays Types

## Slide 2
Translation
Reading More
Translating skills
Text
Basic Relays Types
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types

## Slide 3
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
Basic Relays Types

## Slide 4
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
There are several possible ways to classify relays: by function, by construction, by application.
Relays are one of two basic types of construction: electromagnetic or solid state.
The electromagnetic type relies on the development of electromagnetic forces on movable members, which provide switching action by physically opening or closing sets of contacts.

## Slide 5
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
The solid state provides switching action with no physical motion by changing the state of serially connected solid state component from nonconducting to conducting (or vice versa) .
Electromagnetic relays are older and more widely used; solid state relays are more versatile, potentially more reliable, and fast.

## Slide 6
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
In structure, relays can be classified as follows:
1) Moving-Armature Relay. The moving-armature relay is shown in Fig. 8-1(a). A coil C is wound on a core of magnetic material M. A movable armature A carries with it a movable contact B.
With no current in the coil, the contact B rests against the contacts 1-1, connecting them together. Gravity or spring holds the armature in the position shown.

## Slide 7
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
If current through the coil is slowly increased, a point is reached at which the armature A suddenly rotates to the left, opening contacts 1-1 and closing contacts 2-2. The minimum current at which this motion may be initiated is termed the pickup current.
If the current is now slowly reduced, a value will be found at which the armature will drop back to its original position. This is termed the drop-out, or release, value.

## Slide 8
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
2) Solenoid. A solenoid relay is shown in Fig.8-1(b). A fixed coil surrounds a movable iron plunger. The plunger is held away from a symmetrical position in the coil by gravity or by a spring.
When current of sufficient value flows in the coil, the iron core is drawn into the coil, thus closing the contacts by a simple position change.
Again the pickup current is greater than the release current. The plunger in any selected position experiences a force proportional to the square of the current (or to the square of the voltage across the coil).

## Slide 9
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
3) Balance Beam. An iron armature is fastened to a balance beam as shown in Fig.8-1(c).
The armature is drawn into a fixed-position coil when current flows in the coil.
Various contact and spring arrangements are possible.

## Slide 10
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
4) Mutually Interacting Coils. Two coils, one fixed and one movable, are positioned so that their magnetic fields interact (Fig.8-1d).
If the currents are of constant direction, the force between them will be proportional to the algebraic product of two currents and may result in drawing the coils together or thrusting them apart.
If ac currents flow in the coils, the force action will be proportional to the product of the two current values and the cosine of the angle between them:
4）利用线圈间相互作用构成的继电器。两个线圈，一个固定的，一个是可移动的，如图 8-1（d）所示那样布置，使它们的磁场相互作用。如果线圈中流过的电流方向不变，两个线圈间的作用力正比于两个电流的代数积，并且会将两个线圈吸在一起或因相互排斥而分开。如果线圈中流过的是交流电流，相互间的作用力将正比于这二个电流的大小以及它们之间相位差的余弦的乘积，即

## Slide 11
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
5) Induction Disc or Induction Cup. The induction-disc relay operates on the principle of the induction motor.
As illustrated with Fig.8-l(e), currents displaced in time flowing through coils displaced in space give rise to a moving magnetic field which passes through the movable disc.

## Slide 12
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
This moving magnetic field sets up within the disc currents which result in force action on the disc, tending to make it rotate.
In this type of relay the coils above the disc may carry one current and the coils below the disc carry another current indepen­dently.
If these currents are displaced from each other by the angle, the torque produced on the disc is:

## Slide 13
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
If the two sets of coils are in series and so carry the same current, no torque results. However, a resistor or a capacitor in parallel with one set of coils causes its current to shift out of phase with the other and so gives rise to torque. Other methods of phase shifting are used.
The coils of induction relays are usually provided with taps which enable the selection of pickup current. This permits proper protection coordination even after changes in load layout have taken place during years of service.
如果这二套线圈是相互串联的，因此流有相同的电流，则无力矩产生，但是通常采用在一组线圈两端并联一个电阻或电容的方法使该线圈中的电流的相位不同于另一组线圈中的电流，从而产生力矩，当然也可以采用其他方法来移相。感应继电器的线圈通常提供抽头，用来选择不同的始动电流。这样，即使在多年使用中负荷的布局发生了改变，仍能将保护调整得与之相适应。

## Slide 14
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types

## Slide 15
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types

## Slide 16
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types

## Slide 17
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
New words and phrases
serially ['siəriəli] adv. 逐次地，连载地，串行地
contact ['kɔntækt] n. 接触器; 电气接头; 触头
versatile ['vɜ:sətail] adj. 多用途的, 多功能的
conduct ['kɔndʌkt] v. 传导; 引导; 控制; 操纵
spring [spriŋ] n. 弹簧; 发条
armature ['ɑ:mətʃə] n. 电枢; 转子; 电枢线圈; 衔铁线圈
interact [,intə'ækt] v. 相互作用; 相互影响
rotate [rəu'teit] v. 旋转;转动
torque [tɔ:k] n. 扭转力; 转力矩
resistor [ri'zistə] n. 电阻器
capacitor [kə'pæsitə] n. 电容器
coordination [kəu,ɔ:di'neiʃən] n. 协调

## Slide 18
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
layout ['leiaʊt] n. 规划；编排；布局
mutually ['mju:tʃuəli ] adv. 相互地;彼此地
tap [tæp] n. 抽头
plunger ['plʌʒə]可动铁芯; 活塞
rely on 依赖, 依靠; 信任
give rise to 导致
be proportional to 与…成比例
vice versa 反之亦然
be fastened to被固定于…

## Slide 19
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
Technical Terms
pickup current 始动电流
drop-out current 释放电
release current 释放电流
solenoid relay 螺管式继电器
symmetrical position 平衡位置
balance beam 平衡杆
mutually interacting coils 相互作用线圈
algebraic product 代数乘积
induction-disc relay 感应圆盘式继电器

## Slide 20
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
Language points
1. If current through the coil is slowly increased, a point is reached at which the armature A suddenly rotates to the left, opening contactsl-1 and closing contacts2-2.
句中有一个介词＋关系代词构成的定语从句at which the armature A suddenly rotates to the left. 处于句子结构上的需要，该从句与其被修饰词a Point 之间隔着主句谓语is reached。（在后面的文章中还有几处类似的语法现象出现。）
从句之后的两个并列的现在分词短语opening contacts1-1and closing contacts2-2可理解为定语从句的状语，表示结果。

## Slide 21
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
2. As illustrated with Fig.8-l(e), currents displaced in time flowing through coils displaced in space give rise to a moving magnetic field which passes through the movable disc. This moving magnetic field sets up within the disc currents which result in force action on the disc, tending to make it rotate.
这段文字由两个逻辑关系干分紧密的句子组成，不可将它们分开理解。
在第二个句子的主语currents之后有两个修饰成份，一个是过去分词短语displaced in time，另一个是现在分词短语 flowing through coils displaced in space。 coils之后的过去分词短语displaced in space是coils 的定语。
第二个句子中的定语从句which result in force action on the disc, tending to make it rotate 修饰 the disc currents。从句后的分词短语tending to make it rotate可看作从句的状语，表示结果。

## Slide 22
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
Exercises
I．Answer the following questions according to the text．
1. What’s the difference between an electromagnetic relay and a solid
state relay?
2. How does the moving-Armature Relay work?
3. How many kinds of relays are there by classifying them in
structure, and what are they?
4. What’s the relationship between the force that the plunger
experiences and the current in a solenoid relay?

## Slide 23
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
II．Judge the following are true (T) or false (F) according to the text．
1. The solid state relies on the development of electromagnetic forces on movable members, which provide switching action by physically opening or closing sets of contacts. ( )
2. The plunger of a solenoid relay in any selected position experiences a force proportional to the voltage across the coil. ( )
3. When a moving-armature relay works, the minimum current at which this motion may be initiated is termed the release current. If the current is now slowly reduced, a value will be found at which the armature will drop back to its origi­nal position. This is termed the pickup value. ( )
1.F 2.F 3.F

## Slide 24
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
4. when a mutually Interacting coil works, if direct current
flows in the coils, the force action will be proportional to
the algebraic product of two currents. ( )
5. Various contact and spring arrangements can be used
in the balance beam relays. ( )
4.T 5.T

## Slide 25
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
III. Translate the following terms into English.
1. 电磁继电器
2. 固态继电器
3. 可动衔铁式继电器
4. 释放电流
5. 始动电流
6. 螺线管式继电器
7. 平衡杆式继电器
8. 利用线圈间相互作用构成的继电器
9. 感应圆盘式继电器
10. 可动圆盘
Ex. III.
1. electromagnetic relay
2. solid state relay
3. moving-armature relay
4. release current
5. pick-up current
6. solenoid relay
7. balanced beam type relay
8. mutually interacting coil
9. induction disc relay
10. movable disc

## Slide 26
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
IV．Translate the following sentences into English．
1. 一切物体都能在某种程度上传热,但许多固体比液体传热性能好,而液体又比气体好。
2. 行星在围绕太阳旋转的同时，也绕着它们的自转轴自转。
3. 电流与电压成正比,与电阻成反比。
4. 这些恶劣的环境已造成了许多犯罪行为。
Ex. IV.
1. All bodies of matter conduct heat to some degree. But many solids conduct
heat better than do liquids, and liquids better than gases.
2. Planets revolve about the sun and rotate on their axis.
3. Electric current is directly proportional to voltage and inversely proportional
to resistance.
4. These bad conditions have give rise to a lot of crime.

## Slide 27
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
Translating Skills
科技英语词汇的结构特征（I）
科技英语词汇来源如下。
(1) 来自英语中的普通词汇，但在科技英语中被赋予了新的词义。例如：Work is the transfer of energy expressed as the product of a force and the distance through．Which its point of application moves in the direction of the force．在这句话中，“work”，“energy”，“product”，“force”都是从普通词汇中借来的物理学术语。“work”的意思不是“工作”，而是“功”；“energy”的意思不是“活力”，而是“能”；“product”的意思不是“产品”，而是“乘积”；“force”的意思不是“力量”，而是“力”。

## Slide 28
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
(2) 来自希腊或拉丁语等语言。
例如：therm—热(希腊语)，thesis一论文(希腊语)，parameter—参数(拉丁语)，radius一半径(拉丁语)。
这些来源于希腊语和拉丁语的词的复数形式有些仍按原来的形式，如thesis的复数形式是theses，stratus的复数形式是strati；但由于在英语里使用时间较长，不少词除保留了原来的复数形式外，又采用了英语的复数形式，例如：formula(公式，拉丁语)的复数形式可以是formulae，也可以是formulas，stratum的复数形式(层，拉丁语)可以是strata，也可以是stratums。特别有意思的是，datum(数据，拉丁语)的复数形式是data，但是由于这个词经常用复数，所以有些外国人甚至误把它当成单数，又造出了一个所谓的复数形式datas。
(3) 新出现的词汇。每当出现新的科学技术现象时，人们都要通过词汇把它表示出来，这就需要构造新的词汇。构造新词主要有以下几种方法。

## Slide 29
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
① 转化: 通过词类转化构成新词。英语中名词、形容词、副词、介词可以转化成动词，动词、形容词、副词、介词可以转化成名词；但最活跃的是名词转化成动词和动词转化成名词。例如，名词island(小岛)转化成动词island(隔离)，动词coordinate(协调)转化成名词coordinate(坐标)。
② 合成: 由两个独立的词合成为一个词。例如：air＋craft—aircraft(飞机)，air＋port—airport(机场)，metal＋work—metalwork(金属制品)，power＋plant—powerplant(发电站)。
有的合成词的两个成分之间要有连字符，例如，cast-iron(铸铁)，conveyer-belt(传送带)，machine-made(机制的)。英语中有很多专业术语由两个或更多的词组成，叫做复合术语。它们的构成成分虽然看起来是独立的，但实际上合起来构成一个完整的概念；因此应该把它们看成是一个术语。
例如：1iquid crystal一液晶，water jacket一水套，computer language一计算机语言，machine building一机器制造，linear measure一长度单位，civil engineering一土木工程。

## Slide 30
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
③ 派生: 这种方法也叫缀合。派生词是由词根加上前缀或后缀构成的。构成新词，只改变词义，不改变词性。例如：
decontrol(取消控制) v．—de+control(control是动词)；
ultrasonic(超声的) a．—ultra+sonic(sonic是形容词)；
subsystem(分系统) n．—sub+system(system是名词)。
有些加前缀的派生词在前缀和词根之间有连字符，例如，hydro-electric(发电)，extraterretrial(行星际的)。英语的前缀是有固定意义的，记住其中的一些常用前缀对于记忆生词和猜测词义有帮助。这里只举一些表示否定的前缀来说明问题，例如：anti-表示“反对”，antibody(抗体)；counter-表示“反对，相反”，counterbalance(反平衡)；contra-表示“反对，相反”，contradiction（矛盾)；de-表示“减少，降低，否定，去除”，decrease(减少)，devalue(贬值)，decode(解码)；dis-表示“否定，除去”，discharge(放电)，disassemble(拆卸)；in，il(单词首字母为l)表示“不”，inaccurate(不准确的)；im-(在字母m、b、p前)表示“不”，imbalance(不平衡的)，impure(不纯的)；mis-表示“错误”，mislead(误导)；non-表示“不，非”，non-ferrous(有色金属的)；un-表示“不，未，丧失”，unaccountable(说明不了的)，unknown(未知的)，unbar(清除障碍)。

## Slide 31
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
加后缀构成新词可能改变也可能不改变词义，但一般改变词性。例如：
electricity n．—electric＋ity(electric是形容词)；
liquidize(液化) v．—liquid＋ize(1iquid是名词)；
conductor n．—conduct＋or(conduct是动词)；
invention n．—invent＋ion(invent是动词)。
有的派生词加后缀的时候，语音或拼写可能发生变化。例如：
simplicity(单纯) —simple＋icity；
maintenance(维修)—maintain＋ance；
propeller(推进器)—propel＋l＋er。

## Slide 32
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
英语后缀的作用和前缀有所不同，它们主要用来改变词性。从一个词的后缀可识别它的词类，这是它的语法意义。它们的词汇意义往往并不明显，下面是一些常见的形容词后缀。例如：
-able，-ible，-uble表示“可……的”，avoidable(可以避免的)，audible(听得见的)，soluble(可溶的)；
-al，-ant，ent，表示属性、性质，译为“……的”，fundamental(基本的)，abundant(富饶的)，apparent(显然的)；
-ed，表示“有……的”，cultured(有文化的)；
-ful，表示“充满……的，有……倾向的”，useful(有用的)；
-ic，ieal，形容词尾，basic(基本的)，economical(经济的)；
-less，表示“没有”，useless(无用的)；
-ous，形容词尾，numerous(众多的)；
-let，表示“小的”，booklet(小册子)，wavelet(小波)。

## Slide 33
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
Fault-clearing Protective Relays

## Slide 34
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
Overcurrent relaying. Slow-speed relays. The most obvious effect of a fault is to change the current in the faulted conductor from a normal value to an abnormally large one. Therefore it is not surprising that the earliest methods of clearing faults were based on the utilization of that effect (overcurrent). Early methods included fuses, circuit breakers with series trip coils, and slow-speed overcurrent relays.
现在来谈谈过电流继电保护装置，特别是延时过电流继电保护装置。故障出现时，最明显的变化是故障导体中的电流由正常的电流值变为非正常的大电流。因此，故障切除所采用的早期方法就是以电流的变化为依据。早期所使用的手段包括熔丝、串联跳闸线圈断路器和延时过电流继电器。

## Slide 35
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
Slow-speed overcurrent relays are mostly of the induction type. To obtain selectivity without unnecessarily long delay, such relays usually have a delay which varies inversely with the current. Both time and current settings are adjustable. Since the fault current decreases, on account of the increased impedance of the line between the fault and the source, as the fault is moved farther from the source of power, it follows that the relay operating time increases as the distance to the fault increases.
延时过电流继电器大都是感应型，为了满足选择性和速动性，这种继电保护器通常具有反时限特性。时间和电流整定都具有可调性，由于故障电流较小，当故障离电源较远时，考虑到故障与电源之间线路的阻抗较大，继电器的动作时间会随着故障距离的增加而延长。

## Slide 36
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
The time-distance curves change with such conditions as connected generating capacity and the connection or disconnection of other transmission lines, and therefore, to ensure selectivity, curves should be checked for several conditions to ascertain that, under the worst condition, an adequate interval exists between the operating times of relays1 and3, and, similarly, between each pair of relays on adjoining line sections. Coordination may be accomplished by judicious choice of both time settings and current settings.
时间与距离曲线是依据连接的发电容量与以其他线路连接或中断的状态而变化的。因此，为确保选择性应校验曲线，保证在严重的状态下，1号和3号继电器动作时间之间有适当的时间间隔。在相邻的线路上每一对继电器之间也同样要有时间间隔，这种配合通过恰当选择时间与电流的整定值来完成。

## Slide 37
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
If the relay current changes but little with fault location, the curve of relay time versus fault position becomes more like curve a than like curve b. Such a condition is likely to exist if the impedance of the protected section is small compared with the impedance between the generators and the protected section, as may well be true if the section is short and is fed solely or principally from one end. Moreover curve a may hold even though the relay current does change with fault location, if, as is usually true, the relays are operating on the minimum-time part of their time-current characteristic. Curve a represents an undesirable condition when several protected line sections are in cascade, because the relay time of the lines near the source of power becomes increasingly long.
假如继电器中的电流由于故障而改变，但变化不大，那么故障点对应的时间的曲线变化与a曲线更相像。假如被保护线路的阻抗与发电机和保护线路之间的阻抗相比较小时，就能呈现与a曲线相似的这样一种状态。如线路较短，又是单电源供电或主要从一端供电，情况也是如此。此外，即使继电器中的电流随故障点变动而改变，a曲线仍可能保持不变。如果继电器进行瞬时动作，通常情况也是如此。当几条被保护线路进行串联时，a曲呈现着不理想的状态，因为靠近电源的线路继电器动作时间相应变长。

## Slide 38
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
If a line section is long or has power sources at each end, the relay current will vary considerably with fault location. But, even if the current varies enough to give a curve like b, the operating time of a relay near the generator is usually somewhat longer than that of a relay farther from the generator, though not so much longer as in curve a.
如果一条线路较长或每一端都有电源，继电器的电流就会随故障点的不同将作相应的改变。但即使电流的改变足以像b曲线，靠近发电机的继电器动作时间也比距发电机较远的继电器动作时间长，但不如a曲线的时间长。

## Slide 39
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
By the use of graded time settings, overcurrent relays can always be made to work selectively on a radial transmission or distribution system. With graded settings, and with the addition of directional relays, overcurrent relays can be made to work selectively on a loop system fed from one point. But on a loop fed sometimes from one point and sometimes from another , or on a network more complex than a loop , it is difficult , if not impossible , to choose settings for overcurrent relays so that the relays will work selectively for all fault locations and for all operating conditions.
通过采用阶梯时间配置，过电流继电保护装置能在输电系统或配电系统中有选择性地工作，使用阶段配置并利用方向性继电器，过电流继电器从单电源供电系统中有选择性地工作，但在单回线从一端或从另一端供电的线路中，或在一个比一条线路更复杂的网络中，要想使这种继电装置对一切故障和动作状态进行选择性工作，对过电流继电装置的整定值的确定，将不是一件容易的事。

## Slide 40
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
New words and phrases
utilization [,ju:tilai'zeiʃən] n. 使用；利用
fuse [fju:z] n. 保险丝
selectivity [silek'tiviti ] n. 选择
inversely [in'vaisli] adv. 相反地; 倒转地
setting ['setiŋ] n. 安装; 设定; 装置; 镶嵌
adjustable [ə'dʒʌstəbl ] adj. 可调整的, 可调节的
impedance [im'pi:dəns] n. 阻抗；交流电阻
ascertain [,æsə'tein ] vt. 查明; 弄清; 确定
interval ['intəvl] n. 间隔; 幕间；距离
adjoin [ə'dʒɔin] vt. 贴近; 毗连; 毗邻
coordination [kəu,ɔ:di'neiʃən ] n. 同等；协作
judicious [dʒu:'diʃəs ] adj. 有见识的; 明智的
versus ['vɜ:səs] prep. 对, 对抗
solely ['səulli] adv. 独自地; 单独地
undesirable [,ʌndi'zaiərəbl] adj. 不需要的;不想要的
cascade [kæ'skeid] n. 串联级联

## Slide 41
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
considerable [kən'sidərəbl] adj. 相当多的; 相当大的
breaker ['breiks] n. 断路器
series trip coils 串联跳闸线圈
slow-speed overcurrent relays 延时过电流继电保护
on account of 因为；考虑
be accomplished by 由……完成
circuit breaker 回路短路器
fault current 故障电流
time interval 时间间隔
adequate for 足以……
transmission line 馈电线，输电线
time-current characteristic 时间-电流特性
graded time settings 阶梯形时间配制
line to line fault 时间故障

## Slide 42
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
Exercises
I．Answer the following questions according to the text．
1. What are the earliest methods of clearing faults?
2. What are the characteristics of the induction type of the overcurrent
relays?
3. How does the relay operating time change when the fault is moved
farther from the source of power?
4. How can the overcurrent relays be made to work selectively on a radial
transmission or distribution system?

## Slide 43
Basic Relays Types
自动化专业英语
Unit 8 Basic Relays Types
II．Translate the following phrases and expressions．
1. series trip coils
2. slow-speed overcurrent relays
3. on account of
4. circuit breaker
5. fault current
6. time interval
7. transmission line
8. time-current characteristic
9. graded time settings
10. line to line fault
Ex. II.
1. 串联跳闸线圈
2. 延时过电流继电保护
3. 因为；考虑
4. 回路短路器
5. 故障电流
6. 时间间隔
7. 输电线
8. 时间-电流特性
9. 阶梯形时间配制
10. 时间故障

## Slide 44
Thank You!